## Slide 1: Understanding Grid Changes with BUGMAP
(Bottoms Up Grid Model Advanced Profiles)

## Slide 2: The Burning Questions
Is building electrification a grid asset or liability?
When do the loads occur?
Are the loads coincident?
Hourly end-use load profiles generated by building energy models can help find the answers!

## Slide 3: BUGMAP!

## Slide 4: BUGMAP Process
Model Every Building
Identify Building Composition on Circuit
Apply Appropriate Model Profiles
Simulate Future State Scenarios
Determine Circuit Level Impacts
Calibrate at the Circuit Level

## Slide 5
Which Climate Zones Should We Electrify?
Chart: Electrified Space and Water Heating in a Pre-1978 2,000 ft2 House
| CZ06 | CZ08 | CZ09 | CZ10 | CZ13 | CZ14 | CZ15 | CZ16
Summer Peak Load Difference | 0.91759 | -1.4797 | -2.3572 | -3.1221 | -4.1713 | -4.236 | -4.4347 | -2.0993
Winter Peak Load Difference | 0.22483 | 0.043836 | -0.76034 | -2.0041 | -3.3613 | -3.1386 | -3.9519 | 6.2325

## Slide 6
Which Home Vintages Should We Electrify?
Chart: Electrified Space and Water Heating in a 2,000 ft2 House in CEC Climate Zone 10
| Pre-1978 | 1978 | 1984 | 1992 | 1999 | 2001 | 2004 | 2008 | 2013 | 2016 | 2019
Summer Peak Load Difference | -3.1221 | -2.1955 | -2.3665 | -1.6691 | -1.3734 | -0.2553 | -0.13695 | 0.40744 | 0.41556 | 0.6425 | 1.1206
Winter Peak Load Difference | -2.0041 | -0.872 | -0.52738 | 0.057788 | 0.18103 | 1.6128 | 2.3941 | 2.8858 | 3.8915 | 4.1492 | 4.5556

## Slide 7: Location, Vintage, and Square Footage Matter!
Circuit XYZ Housing Stock
Basic Assumptions (homes are mostly pre-1978 and average about 2,000 ft2) Predicted residential cumulative demand = 12.1 MW
Refined Assumptions (precise home sizes and vintages estimates for XYZ Circuit) Predicted residential cumulative demand = 8.7 MW
XYZ Facility Loading Limit is only 11.96 MW

## Slide 8: Ontario Single Family Vintage Map (1979-2020)

## Slide 9: BE Retrofits Improve Circuit Utilization
Time Above 6 kW:
Baseline: 5%
BE Retrofit: 2%
BE Profile Features:
Short duration intense peak load driven by HPWH backup resistance heating elements.
Improved overall utilization driven by HP space heating in winter.

## Slide 10: Thank you!